## All Locations-FINAL
LSP ID | Need Category | Region | Project Type | Title | Solution Description | ISD, Projected | Project Status | Transmission Cost, Estimated ($M) | PPA ID | Changes From Last Year
ES-23-LSP-001 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Burlington Sta #391 - Transformer Addition | Install one 50 MVA 115/14kV mobile transformer | Nov-2023 | Under Construction | N/A | ES-22-T16 | Yes
ES-23-LSP-002 | Asset Condition/ Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Kingston Substation #735 | Station rebuild and redesign. This project listing includes the non-PTF and distribution components of ACL 27.​ | Dec-2023 | Under Construction | 33.4 | ES-23-T02, ES-23-T03 | Yes
ES-23-LSP-003 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transmission Line Project | 115kV Line 117-502 and 117-508 structure replacements and OPGW - Canton Tap | Replace existing structures due to reliability concerns and asset condition | Jun-2024 | Under Construction | 7.2 | N/A | Yes
ES-23-LSP-004 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Somerville #402 - Transformer Addition | Install a 3rd 62.5 MVA transformer at Somerville #402. | Dec-2024 | Under Construction | N/A | TBD | Yes
ES-23-LSP-005 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Medway Substation #65 - Transformer Replacement | Replace the 115/13.8kV 40 MVA 110A transformer with a 62.5 MVA transformer | Dec-2024 | Under Construction | N/A | ES-22-T19 | No Changes
ES-23-LSP-006 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Medway Substation #65 - Transformer Replacement | Replace the 115/13.8kV 40 MVA 110B transformer with a 62.5 MVA transformer | Dec-2024 | Under Construction | N/A | ES-22-T20 | No Changes
ES-23-LSP-007 | Local Reliability | Eastern Massachusetts | Transmission Line Project | Andrew Square Sta #106 to Dewar Sta #483, new 115kV Line | Install new 115kV transmission line between Andrew Square and Dewar stations to provide alternative source to either station under N-1-1 contingencies | Dec-2024 | Under Construction | 96.3 | ES-19-T04 | Yes
ES-23-LSP-008 | Asset Condition/ Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Andrew Square STA #106 | Build new control house and upgrade substation to Bulk Power Station standards​ | Dec-2024 | Under Construction | 26.7 | ES-19-X01 | No Changes
ES-23-LSP-009 | Asset Condition/ Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Dewar St. Sta. #483 | Build new control house and upgrade substation to Bulk Power Station standards​ | Dec-2024 | Under Construction | 24.8 | ES-19-X02 | No Changes
ES-23-LSP-010 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Carver St. Substation #71 - Transformer Replacements | Replace two 115/13.8kV 85 MVA (110A & 110B) transformers with two 90 MVA transformers. Extend the 115kV GIS bus to the new transformers. | 2025 | Under Construction | 9.3 | TBD | No Changes
ES-23-LSP-011 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | East Eagle Substation #131 - New Substation | Install two 115/13.8kV 62.5 MVA transformers at new substation. PTF components of substation are listed under RSP 1745. Substation will be served by bifurcating the Mystic-Chelsea 115 kV that was listed as RSP 1354 and placed in service 10/2020.​ | 2025 | Under Construction | N/A | ES-16-T13 | No Changes
ES-23-LSP-012 | DER Group Study | Eastern Massachusetts | Transmission Line Project | Marion-Fairhaven Group 2022 - Crystal Spring | Extend the 115kV 112 Line from Crystal Spring Junction to Crystal Spring station for the transformer addition at Crystal Spring | 2025 | Planned | 25 | ES-21-T70 | No Changes
ES-23-LSP-013 | DER Group Study | Eastern Massachusetts | Transformer Additions/Replacements | Marion-Fairhaven Group 2022 - Crystal Spring | Replace the Crystal Spring transformer #1 with a new 37/50/62.5 MVA, 115/13.2 kV transformer. Install a new 37/50/62.5 MVA, 115/13.2 kV transformer #2. ​ | 2025 | Planned | 14 | ES-21-T71, ES-21-T72 | No Changes
ES-23-LSP-014 | DER Group Study | Eastern Massachusetts | Transformer Additions/Replacements | Marion-Fairhaven Group 2022 - Rochester | Replace the Rochester transformer #112 with a new 37/50/62.5 MVA, 115/13.2kV transformer​ | 2025 | Planned | 12 | ES-21-T77 | No Changes
ES-23-LSP-015 | DER Group Study | Eastern Massachusetts | Transformer Additions/Replacements | Marion-Fairhaven Group 2022 - Wing Lane | Replace the Wing Lane transformer #1 and #2 with new 37/50/62.5 MVA, 115/13.2kV transformers | 2025 | Planned | 5 | ES-21-T78, ES-21-T79 | No Changes
ES-23-LSP-016 | DER Group Study | Eastern Massachusetts | Transformer Additions/Replacements | Dartmouth-Westport Group - Cross Road and Fisher Road | Replace the Fisher Road transformer #1 and #2 with new 37/50/62.5 MVA, 115/13.2kV transformers | 2025 | Planned | 13 | ES-21-T80, ES-21-T81 | No Changes
ES-23-LSP-017 | DER Group Study | Eastern Massachusetts | Transmission Line Project | Common Upgrade for Multiple Groups: 191 Line | Reconductor the 115kV 191 Line between Auburn Street and Kingston Street with 1590 ACSS. | 2025 | Planned | 27 | ES-21-T51-Rev1 | No Changes
ES-23-LSP-018 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Baker Street Substation - Transformer Replacement (West Roxbury) | Replace the 115/23kV 75 MVA 110A transformer with a 90 MVA transformer | 2025 | Proposed | N/A | TBD | New
ES-23-LSP-019 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Mystic 250 - Transformer Replacement | Replace the 115/24kV 60 MVA 110C transformer with a 115/13.8kV 62.5 MVA | 2025 | Concept | N/A | TBD | No Changes
ES-23-LSP-020 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Rochester Substation #745 - Transformer Replacement | Replace the 115/13.2kV 12.5 MVA #114 transformer with new 62.5 MVA transformer. | 2026 | Planned | N/A | ES-21-T76 | No Changes
ES-23-LSP-021 | DER Group Study | Eastern Massachusetts | Transformer Additions/Replacements | Plymouth Group 2022 - Wareham | Replace Wareham transformer #1 with a 45/60/75 MVA, 115/23 kV transformer. | 2026 | Planned | N/A | ES-21-T63 | No Changes
ES-23-LSP-022 | DER Group Study | Eastern Massachusetts | Substation Reconfiguration/Expansion | Plymouth Group 2022 - West Pond #737 Station | Upgrade the West Pond station to a six-breaker ring bus configuration. Replace transformers #1 and #2 with 45/60/75 MVA, 115/23 kV transformers and install a new 45/60/75 MVA transformer #3. ​ | 2026 | Planned | 25 | ES-21-T66, ES-21-T67, ES-21-T68, ES-21-T69 | No Changes
ES-23-LSP-023 | DER Group Study | Eastern Massachusetts | Transmission Line Project | Plymouth Group 2022 - West Pond Line 132 | Reconductor the 115 kV 132 Line between Brook Street and West Pond with 795 ACSR​ | 2026 | Planned | 23 | ES-21-T65 | No Changes
ES-23-LSP-024 | DER Group Study | Eastern Massachusetts | Transformer Additions/Replacements | Plymouth Group 2022 - Tremont | Replace the Tremont transformer #2 with a new 45/60/75 MVA, 115/23kV transformers. Install a new 45/60/75 MVA, 115/23kV transformer #3 | 2026 | Planned | N/A | ES-21-T74, ES-21-T75 | No Changes
ES-23-LSP-025 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Tremont #713 - Transformer Replacement | Replace the 115/23kV 20 MVA #1 transformer with a 75 MVA | 2026 | Planned | N/A | ES-21-T73 | No Changes
ES-23-LSP-026 | DER Group Study/ Local Reliability | Eastern Massachusetts | Transmission Line Project | Freetown Group 2022 - Bell Rock | Build a new 115kV line from Bell Rock to supply new Assonet four (4) breaker ring configuration for DER Group Study. | 2026 | Planned | 82 | ES-21-T52 | No Changes
ES-23-LSP-027 | DER Group Study/ Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Freetown Group 2022 - Assonet | Build a new 115/13.2kV Assonet station with four-breaker ring configuration. Install two new 37/50/62.5 MVA, 115/13.2kV transformers | 2026 | Planned | 38 | ES-21-T54, ES-23-T59 | Yes
ES-23-LSP-028 | DER Group Study | Eastern Massachusetts | Transmission Line Project | Freetown Group 2022 - 2nd 115kV Line to Assonet | Second 115kV line to the new 115kV Assonet Substation | 2026 | Planned | TBD | ES-23-T58 | Yes
ES-23-LSP-029 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Maynard Station #416 - Transformer Replacement | Replace the 115/13.8kV 50 MVA 110A transformer with a 62.5 MVA transformer | 2026 | Concept | N/A | TBD | No Changes
ES-23-LSP-030 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Waltham Substation - Transformer Replacement | Replace the 115/13.8kV 90 MVA 110B transformer with a 90 MVA transformer | 2026 | Concept | N/A | TBD | New
ES-23-LSP-031 | Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Industrial Park #636 Battery Storage / STATCOM | Interconnect a 5 MW / 10 MWHR BESS with a 25 MVAR STATCOM for power quality improvement for customers out of Industrial Park Substation #636. The interconnection will be made at the 13.2kV side of the substation. | 2026 | Concept | TBD | TBD | New
ES-23-LSP-032 | Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Hyde Park #496 BESS | Interconnect a 15 MW / 20 MWHR Battery Storage System as a non-wires capacity deferral on the 24kV and 13.8kV sides of Hyde Park Substation #496 | 2026 | Concept | TBD | TBD | New
ES-23-LSP-033 | Local Reliability | Eastern Massachusetts | New Substation | Weymouth Substation | Build a new 115 kV three-breaker ring substation Broad Street #624 in Weymouth, MA that will bisect line 478-502. Install a new radial 115 kV, 3.7-mile cable from the new station to provide a new supply to Hingham Municipal. ​ | 2027 | Planned | N/A | ES-23-T53, ES-23-X02 | Yes
ES-23-LSP-034 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transmission Line Project | 115kV Line 126-501/502 XLPE Replacement | Replace pipe-type cable (PTC) circuits between Hopkinton and Milford with solid dielectric cross-linked polyethylene (XLPE) technology | 2027 | Proposed | TBD | TBD | New
ES-23-LSP-035 | Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Maynard Station #416 - Transformer Replacement | Replace the 115/13.8kV 50 MVA 110B transformer with a 62.5 MVA transformer | 2027 | Concept | N/A | TBD | No Changes
ES-23-LSP-036 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Hawkins Street 2 - Transformer Replacement | Replace the 115/13.8kV 62.5 MVA 110A transformer with a 90 MVA transformer | 2027 | Concept | N/A | TBD | Yes
ES-23-LSP-037 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transformer Additions/Replacements | Hawkins Street 2 - Transformer Replacement | Replace the 115/13.8kV 62.5 MVA 110B transformer with a 90 MVA transformer. | 2027 | Concept | N/A | TBD | Yes
ES-23-LSP-038 | Local Reliability | Eastern Massachusetts | New Substation | Hyde Park Substation | Build additional load service capacity in the project area. It is expected that a new transmission substation will be required.​ | 2029 | Concept | TBD | TBD | No Changes
ES-23-LSP-039 | Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Holbrook #478 - Ring Bus Upgrade | Add two breakers at the Holbrook 345kV station to close the ring bus | 2027 | Concept | TBD | TBD | No Changes
ES-23-LSP-040 | Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Alewife Substation #829 Expansion | Install a 4th 62.5 MVA transformer | 2027 | Concept | TBD | TBD | New
ES-23-LSP-041 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transmission Line Project | 115kV Line 142/143 XLPE Replacement | Replace pipe-type cable (PTC) circuits between Acushnet and Pine St with solid dielectric cross-linked polyethylene (XLPE) technology | 2028 | Planned | 198.4 | ES-23-T01 | Yes
ES-23-LSP-042 | DER Group Study | Eastern Massachusetts | Substation Reconfiguration/Expansion | Industrial Park #636 Station Upgrades - Ring Bus, transformer replacements and addition | Upgrade the Industrial Park station to a six-breaker ring bus configuration. Replace transformers #1 and #2 with new 37/50/62.5 MVA, 115/13.2kV transformers and install a new 37/50/62.5 MVA transformer #3 | 2028 | Planned | TBD | ES-21-T58, ES-21-T59, ES-21-T60, ES-21-T61 | No Changes
ES-23-LSP-043 | Local Reliability | Eastern Massachusetts | Transmission Line Project | New Bourne to Falmouth Tap 115kV Line | Install a new 115-kV transmission line between Bourne and Falmouth Tap substation to mitigate Consequential Load Loss violations under N-1-1 conditions. | 2028 | Proposed | TBD | TBD | Yes
ES-23-LSP-044 | Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Falmouth Tap Switching Station Upgrade | Upgrade Falmouth Tap Switching Station from a 1-breaker series bus arrangement to a 115kV breaker and a half scheme. Install a 115/23kV bulk distribution station with one 45/50/75 MVA transformer to address area load growth | 2028 | Concept | N/A | TBD | Yes
ES-23-LSP-045 | Local Reliability | Eastern Massachusetts | New Substation | North Burlington Substation | Build a new 115/14kV station with two 62.5 MVA 115/14kV transformers. | 2028 | Concept | TBD | TBD | Yes
ES-23-LSP-046 | Local Reliability | Eastern Massachusetts | New Substation | Greater Cambridge Energy Program | Install new substation with three (3) 90 MVA 115/14-kV transformers which will relieve East Cambridge #875, Putnam #831 and Prospect St #819 (distribution-only substation). New substation will be supplied via 329-510/511 lines from Brighton which will be replaced with XLPE cables and 329/510-511 lines from Somerville/Mystic, which will be replaced with XLPE as part of ES-23-LSP-047. The existing 831-538 and 875-539 lines will also interconnect with the new substation. Relocate 875-539 terminal to new substation.​ | 2029 | Proposed | TBD | TBD | Yes
ES-23-LSP-047 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transmission Line Project | 115kV Line 329-510/511 XLPE Replacement | Replace pipe-type cable (PTC) circuits between Somerville and Mystic with solid dielectric cross-linked polyethylene (XLPE) technology | 2029 | Proposed | TBD | TBD | No Changes
ES-23-LSP-048 | Local Reliability | Eastern Massachusetts | Transmission Line Project | Newton Highlands #292 Substation Third Transmission Source | Add a third 115 kV line to Newton Highlands 292 substation | 2030 | Concept | TBD | TBD | New
ES-23-LSP-049 | Local Reliability | Eastern Massachusetts | New Substation | Harwhich/Orleans Substation | Install new distribution bulk substation with two (2) 115/23kV 75 MVA transformers. The proposed location is TBD and will most likely be installed at Harwich Tap Switching Station where the 118, 119, and 139 lines tap to Harwich Sub. Previously listed on the LSP as Dennis/Brewster. | 2030 | Concept | TBD | TBD | Yes
ES-23-LSP-050 | Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Electric Ave Substation #315 Expansion | Install a 4th 62.5 MVA transformer | 2030 | Concept | TBD | TBD | New
ES-23-LSP-051 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transmission Line Project | 115kV Line 292-522/523 XLPE Replacement | Replace pipe-type cable (PTC) circuits between Baker St and Newton Highlands with solid dielectric cross-linked polyethylene (XLPE) technology | 2030 | Concept | TBD | TBD | New
ES-23-LSP-052 | Local Reliability | Eastern Massachusetts | Transmission Line Project | Partially Reconstruct 250-516/517 lines | The city of Boston is replacing the North Washington St. bridge. The existing 250-516/517 lines are attached to the bridge. Existing lines are HPFF PTC. Reconstruct 250-516/517 on the new bridge utilizing XLPE cable. | 2031 | Cancelled | 43.6 | ES-22-T09 | Yes
ES-23-LSP-053 | Local Reliability | Eastern Massachusetts | New Substation | Natick Substation | Permanent 115/14kV Station either at Saxonville or Mill Street, Natick with two 65 MVA transformers.​ ​ | 2031 | Concept | TBD | TBD | Yes
ES-23-LSP-054 | Asset Condition/ Local Reliability | Eastern Massachusetts | Transmission Line Project | 115kV Line 250-516/517 XLPE Replacement | Replace pipe-type cable (PTC) circuits between Mystic and Seafood Way with solid dielectric cross-linked polyethylene (XLPE) technology | 2031 | Concept | TBD | TBD | Yes
ES-23-LSP-055 | Local Reliability | Eastern Massachusetts | Substation Reconfiguration/Expansion | Seafood Way Substation #99 Expansion | Install a 4th 62.5 MVA transformer | 2033 | Concept | TBD | TBD | New
ES-23-LSP-056 | Local Reliability | Eastern Massachusetts | New Substation | New Metro Boston Network Station | A new downtown Boston area substation to supply the secondary network systems | 2034 | Concept | TBD | TBD | New
ES-23-LSP-057 | Local Reliability | Eastern Massachusetts | New Substation | New East Allston / Fenway/Brookline Substation | A new bulk distribution substation to supply the Allston / Fenway / Brookline areas of Metro Boston | 2034 | Concept | TBD | TBD | New
ES-23-LSP-058 | Local Reliability | Eastern Massachusetts | New Substation | New Charlestown / Somerville Substation | A new bulk distribution substation to supply the Somerville/Charlestown areas of Metro Boston | 2034 | Concept | TBD | TBD | New
ES-23-LSP-059 | Local Reliability | Eastern Massachusetts | New Substation | New Waltham Substation | A new bulk distribution substation in Waltham to relieve the existing North and West Waltham Substations. | 2034 | Concept | TBD | TBD | New
ES-23-LSP-060 | Local Reliability | Eastern Massachusetts | New Substation | New South End Substation | A new bulk distribution substation in South End/Andrew Square neighborhoods of Metro Boston | 2034 | Concept | TBD | TBD | New
ES-23-LSP-061 | Local Reliability | Eastern Massachusetts | New Substation | Future North Acton Substation | Install new distribution bulk substation. The proposed location is in the vicinity of North Acton | 2034 | Concept | TBD | TBD | New
ES-23-LSP-062 | Local Reliability | Western Massachusetts | Transmission Line Project | Fairmont-Montague corridor transmission supply upgrade | Rebuild the 115kV transmission lines supplying the Amherst, Tilson, Podick, and Five Corners load pocket. Remove existing Type III Special Protection System | Nov-2022 | In-Service | 136.4 | ES-20-T08, ES-20-T09, ES-20-T10, ES-20-T11 | Yes
ES-23-LSP-063 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Clinton Substation - Transformer Replacement | Replace existing 115/13.8kV 30 MVA 3X transformer with a 62.5 MVA transformer | Jun-2023 | In-Service | N/A | ES-21-T97 | Yes
ES-23-LSP-064 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Breckwood Substation - Transformer Replacement (Springfield) | Replace existing 115/13.8kV 30 MVA 1X transformer with a 62.5 MVA transformer | Jun-2023 | In-Service | N/A | ES-21-T94 | Yes
ES-23-LSP-065 | Asset Condition | Western Massachusetts | Transmission Line Project | 115kV Line 1715/1816 Copper Conductor Replacement Rebuild | Replace deteriorating structures, obsolete conductor, and shield wire. Remove existing Type III Special Protection System. | Aug-2023 | In-Service | 17.3 | ES-22-T43, ES-22-T44 | Yes
ES-23-LSP-066 | Asset Condition/ Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Montague Substation - Transformer Replacement | Replace existing 115/13.8kV 30 MVA 3X transformer with a 62.5 MVA transformer | Mar-2024 | Proposed | N/A | TBD | No Changes
ES-23-LSP-067 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Franconia Substation - Transformer Replacement | Replace existing 115/13.8kV 47 MVA 2X transformer with a 62.5 MVA transformer | Oct-2024 | Planned | N/A | ES-21-T98 | Yes
ES-23-LSP-068 | Asset Condition/ Local Reliability | Western Massachusetts | Transmission Line Project | Line 1231/1242 Upgrade Project - Associated Upgrades | Terminal structure replacements and ADSS installation at line terminal substations, Ashfield and Plainfield. NonPTF work associated with ACL 250. | Nov-2024 | Planned | 13.1 | N/A | New
ES-23-LSP-069 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Clinton Substation - Transformer Replacement | Replace existing 115/13.8kV 30 MVA 2X transformer with a 62.5 MVA transformer | 2025 | Planned | N/A | ES-21-T99 | Yes
ES-23-LSP-070 | Asset Condition/ Local Reliability | Western Massachusetts | Transmission Line Project | 115kV Line 1544/1755 XLPE Replacement | Replace pipe-type (PTC) circuits between Clinton and West Springfield with solid dielectric cross-linked polyethylene (XLPE) technology. | 2026 | Planned | TBD | ES-22-T45, ES-22-T46 | Yes
ES-23-LSP-071 | DER Group Study/Reliability | Western Massachusetts | Substation Reconfiguration/Expansion | Blandford Substation - Transformer Replacements | Replace existing 115/23kV 1X (30 MVA) and 2X (25 MVA) transformers with 62.5 MVA transformers. | 2025 | Proposed | N/A | TBD | No Changes
ES-23-LSP-072 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Plainfield Substation - Transformer Replacement | Replace existing 115/13.8kV 30 MVA 1X transformer with a 62.5 MVA transformer | 2025 | Proposed | N/A | TBD | Yes
ES-23-LSP-073 | Asset Condition/ Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Clinton Substation - Transformer Replacement | Replace existing 115/13.8kV 30 MVA 1X transformer with a 62.5 MVA transformer | 2026 | Concept | N/A | TBD | Yes
ES-23-LSP-074 | Asset Condition/ Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Pleasant Substation - Transformer Replacement | Replace existing 115/13.8kV 30 MVA 2X transformer with a 62.5 MVA transformer | 2026 | Concept | N/A | TBD | Yes
ES-23-LSP-075 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Ludlow Substation - Transformer Addition | Install new 115/13.8kV 62.5 MVA 2X transformer | 2026 | Concept | N/A | TBD | Yes
ES-23-LSP-076 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | West Springfield Substation - Transformer Replacement | Replace existing 115/13.8kV 30 MVA 1X transformer with a 62.5 MVA transformer | 2026 | Concept | N/A | TBD | Yes
ES-23-LSP-077 | Asset Condition/ Local Reliability | Western Massachusetts | Transformer Additions/Replacements | West Springfield Substation - Transformer Replacement | Replace existing 115/13.8kV 30 MVA 2X transformer with a 62.5 MVA transformer | 2026 | Concept | N/A | TBD | No Changes
ES-23-LSP-078 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Partridge Substation - Transformer Addition | Install new 115/23kV 62.5 MVA 2X transformer | 2026 | Concept | N/A | TBD | New
ES-23-LSP-079 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Silver Substation - Transformer Replacement | Replace existing 115/13.8kV 47 MVA 1X transformer with a 62.5 MVA transformer | 2027 | Concept | N/A | TBD | Yes
ES-23-LSP-080 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Silver Substation - Transformer Replacement | Replace existing 115/13.8kV 47 MVA 2X transformer with a 62.5 MVA transformer | 2027 | Concept | N/A | TBD | New
ES-23-LSP-081 | Asset Condition/ Local Reliability | Western Massachusetts | Transmission Line Project | 115kV Line 1322 XLPE Replacement | Rebuild the existing 1322 Line HPFF between Breckwood SS (Springfield) and East Springfield SS cable system with solid dielectric cross-linked polyethylene (XLPE) technology. | 2028 | Proposed | TBD | TBD | Yes
ES-23-LSP-082 | Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Franconia Substation - Transformer Replacement | Replace existing 115/13.8kV 47 MVA 3X transformer with a 62.5 MVA transformer | 2028 | Concept | N/A | TBD | Yes
ES-23-LSP-083 | Asset Condition/ Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Woodland Substation - Transformer Replacement | Replace existing 115/23kV 25 MVA 1X transformer with a 62.5 MVA transformer | 2028 | Concept | N/A | TBD | No Changes
ES-23-LSP-084 | Asset Condition/ Local Reliability | Western Massachusetts | Transformer Additions/Replacements | Midway Substation - Transformer Replacement | Replace existing 115/13.8kV 20 MVA 1X, 2X, and 3X Y-D transformer with a 62.5 MVA D-Y transformer | 2028 | Concept | N/A | TBD | No Changes
ES-23-LSP-085 | Asset Condition/ Local Reliability | Western Massachusetts | Transmission Line Project | 115kV Line 1433 XLPE Replacement | Rebuild the existing 1433 Line HPFF between Breckwood SS (Springfield) and West Springfield SS cable system with solid dielectric cross-linked polyethylene (XLPE) technology. | 2029 | Proposed | TBD | TBD | Yes
ES-23-LSP-086 | Local Reliability | Western Massachusetts | New Substation | Worthington Street Substation | Build a new 115/13 kV station (Worthington St. Substation) in Springfield with two 62.5MVA 115/13.8kV transformers. Add 115kV transmission circuit from Clinton and a 115kV transmission circuit from East Springfield with some terminal work at both stations. Reconfigure Cadwell Station with the addition of a single circuit breaker.​ | 2030 | Concept | TBD | TBD | Yes
ES-23-LSP-087 | Local Reliability | Western Massachusetts | New Substation | Whately/Hatfield Substation | Build a new 115/13.8kV substation (Whately-Hatfield Substation) in Whately-Hatfield area with two 62.5 MVA 115/13.8-kV transformers. Add two 115-kV transmission circuits connecting the new substation to the transmission system with possibly one from Cumberland and one from Podick with terminal work at same stations. ​ | 2030 | Concept | TBD | TBD | Yes
ES-23-LSP-088 | Local Reliability | Western Massachusetts | New Substation | Hilltown Substation | Build a new 115/23kV substation (Hilltown Substation) in Worthington/Chester area with two 62.5 MVA 115/23-kV transformers. Add two 115-kV transmission circuits connecting the new substation to the transmission system with possibly one from Plainfield 18K and one from Blandford with terminal work at same stations. ​ | 2030 | Concept | TBD | TBD | New
ES-23-LSP-089 | Asset Condition | Connecticut | Transmission Line Project | 1210 and 1220 115kV Line Structure Replacements and Optical Ground Wire (OPGW) Installation | Replace existing structures due to Asset Condition and install OPGW | Nov-2022 | In-Service | 6.4 | N/A | Yes
ES-23-LSP-090 | Local Reliability | Connecticut | Transformer Additions/Replacements | East Meriden - Transformer Replacement Project | Replace 115/13.8kV 46.7 MVA 1X transformer with 62.5 MVA transformer. | Dec-2022 | In-Service | N/A | ES-22-T26 | Yes
ES-23-LSP-091 | Local Reliability | Connecticut | Transformer Additions/Replacements | Montville 69kV Backup Supply | Install one 115/69kV autotransformer at Montville 69kV to provide backup to Station Service. | Mar-2023 | In-Service | 11.5 | ES-22-T41 | Yes
ES-23-LSP-092 | Asset Condition/Local Reliability | Connecticut | Transmission Line Project | 115kV Lines 1100/1200/1300 - OPGW and Reconductor CT River Crossing | Replace deteriorating copper and alumoweld shield wire with OPGW as well as deteriorating copper conductor with 1590 ACSS conductor | Apr-2023 | In-Service | 15 | N/A | Yes
ES-23-LSP-093 | Local Reliability | Connecticut | Transformer Additions/Replacements | Ridgefield Substation - Transformer Replacements | Replace two 115/13.8kV 46.7 MVA transformers with two new 62.5 MVA transformers. | May-2023 | In-Service | N/A | ES-22-T13, ES-22-T14 | Yes
ES-23-LSP-094 | Asset Condition/Local Reliability | Connecticut | Transmission Line Project | 115kV Line 500 Copper Retirement | Replace deteriorating copper materials with ACSS conductor and OPGW shield wire | Jun-2023 | In-Service | 24.3 | ES-23-T38 | Yes
ES-23-LSP-095 | Local Reliability | Connecticut | Transformer Additions/Replacements | Carmel Hill Substation - Transformer Addition | Add a second 115/23kV transformer 62.5 MVA to the substation to increase capacity and improve reliability. | Oct-2023 | In-Service | 6.8 | ES-21-T01 | Yes
ES-23-LSP-096 | Local Reliability | Connecticut | Transformer Additions/Replacements | Mansfield Substation - Transformer additions and removal | Install two 115/23kV, 62.5 MVA transformers and eliminate the single 115/27.6kV 30 MVA transformer. | Dec-2023 | Under Construction | 14.6 | ES-20-T02 | Yes
ES-23-LSP-097 | Local Reliability | Connecticut | Substation Reconfiguration/Expansion | Gales Ferry Substation - Rebuild substation and add transformers | Convert substation from 69 kV to 115 kV. Replace existing transformers with two new 62.5 MVA transformers.​ This project listing includes the non-PTF and distribution components of RSP 1856-1859 and 1864​ | Dec-2023 | Under Construction | N/A (Transmission costs listed on RSP) | ES-21-T33 | No Changes
ES-23-LSP-098 | Local Reliability | Connecticut | Transformer Additions/Replacements | Sandy Hook Substation - Transformer addition (Newtown) | Add a second 115/23kV transformer 62.5 MVA to the substation to increase capacity and improve reliability. | Dec-2023 | Under Construction | N/A | ES-21-T101 | Yes
ES-23-LSP-099 | Local Reliability | Connecticut | Transformer Additions/Replacements | Sasco Creek Substation | Replace two 115/27.6kV 15 MVA 1X and 2X transformers with two 115/26.4kV 30 MVA transformers. | Mar-2024 | Proposed | N/A | N/A | Yes
ES-23-LSP-100 | Asset Condition/Reliability | Connecticut | Transmission Line Project | 1163 and 1550 - Tap Project | The project is a rebuild of Line 1163-3 and 1550-2 replacing 3 miles (1.5-miles per circuit) of existing 4/0 copper conductor with 1272-kcmil ACSS conductor. | Apr-2024 | Planned | 13.3 | 2/23/2023 | New
ES-23-LSP-101 | Local Reliability | Connecticut | Transformer Additions/Replacements | Salisbury Substation - Transformer Replacement | Replace 69/13.2kV 13 MVA transformer with 62.5 MVA transformer. | Aug-2024 | Proposed | N/A | TBD | Yes
ES-23-LSP-102 | Local Reliability | Connecticut | Transmission Line Project | Campville 14R - Circuit Breaker and 1788-1900 Single DCT Split | Install 115-kV series circuit breaker 4TA and split the single 1788/1900 double circuit tower (DCT)​. | Dec-2024 | Planned | TBD | ES-23-T29 | Yes
ES-23-LSP-103 | Local Reliability | Connecticut | Transmission Line Project | Norwalk-CDOT replace structures at Norwalk River crossing (Norwalk) | The project consists of relocating two existing 115-kV transmission lines from an overhead portion of the railroad corridor to underground. The new underground sections will, for both circuits, consist of approximately 1,200 feet of trenched duct bank on the West side of the Norwalk River, approximately 1,100 feet of HDD underneath the Norwalk River, and approximately 2,200 feet of trenched duct bank on the East side of the Norwalk River. Also, two short overhead railroad crossings of approximately 177 feet and 108 feet, respectively, are required on the 1028 line.​ | 2025 | Under Construction | $46.4 (Approximately 50% reimbursable) | TBD | Yes
ES-23-LSP-104 | Local Reliability | Connecticut | Substation Reconfiguration/Expansion | Bunker Hill Substation Reconfiguration (Waterbury) | Addition of three (3) new 115-kV circuit breakers and reconfigure the Bunker Hill 115 kV substation into a six-breaker ring bus including substation modifications.​ | 2025 | Planned | 19.4 | ES-21-T18 | Yes
ES-23-LSP-105 | Asset Condition/Local Reliability | Connecticut | Transmission Line Project | 115kV Line 1690 Copper Retirement | Replace deteriorating copper materials with ACSS conductor and OPGW shield wire | 2025 | Planned | 24.7 | ES-23-T35 | Yes
ES-23-LSP-106 | Asset Condition/Local Reliability | Connecticut | Transformer Additions/Replacements | Hopewell - Transformer Replacements | Replace two 115/23kV 46.7 MVA transformers with two new 62.5 MVA transformers. | 2025 | Planned | N/A | ES-22-T30, ES-22-T31 | Yes
ES-23-LSP-107 | Local Reliability | Connecticut | Transformer Additions/Replacements | Bokum Substation - Transformer Replacements | Replace two 115/27.6kV 50 MVA transformers with two 62.5 MVA transformers. | 2025 | Planned | N/A | ES-21-T90 | No Changes
ES-23-LSP-108 | Asset Condition/Local Reliability | Connecticut | Transformer Additions/Replacements | Beacon Falls - Transformer Replacements | Replace two 115/13.8kV 46.7 MVA transformers with 62.5 MVA transformers. | 2025 | Planned | N/A | ES-22-T24, ES-22-T25 | Yes
ES-23-LSP-109 | Asset Condition/Local Reliability | Connecticut | Transmission Line Project | 115kV Line 1820/1830/1670-3 - Copper Conductor Replacement/Rebuild | Replace deteriorating structures and obsolete conductor from Southington substation to Blackrock substation | 2025 | Proposed | TBD | TBD | Yes
ES-23-LSP-110 | Local Reliability | Connecticut | Transformer Additions/Replacements | Southington Substation - Transformer Addition | Add a 115/13.8kV 62.5 MVA transformer to increase capacity and improve reliability. | 2025 | Proposed | N/A | TBD | Yes
ES-23-LSP-111 | Local Reliability | Connecticut | Transformer Additions/Replacements | Franklin Drive Substation - Transformer Replacements | Replace 115/13.2kV 25 MVA 4X and 5X transformers with 62.5 MVA transformers. | 2025 | Concept | N/A | TBD | No Changes
ES-23-LSP-112 | Asset Condition/Reliability | Connecticut | Transformer Additions/Replacements | North Canaan - Transformer Replacement and Reconfiguration | Replace the existing wye-wye transformer with a delta-wye to match the surrounding area and improve reliability. Add new feeder position. Replace aging infrastructure. | 2025 | Concept | TBD | TBD | No Changes
ES-23-LSP-113 | Local Reliability | Connecticut | Substation Reconfiguration/Expansion | Falls Village Substation - Reconfiguration | Replace 69/13.2kV 25 MVA transformer with 40 MVA transformer. Reconfigure existing switchyard by replacing 2 existing and adding 6 new circuit breakers. | 2026 | Planned | TBD | ES-22-T01 | Yes
ES-23-LSP-114 | Local Reliability | Connecticut | Transformer Additions/Replacements | Devon Railroad - Oil Circuit Breaker and Transformer Replacement Project | Upgrades to the Devon Railroad substation associated with Metro North and CDOT | 2026 | Proposed | N/A | TBD | Yes
ES-23-LSP-115 | Asset Condition | Connecticut | Transmission Line Project | Line 680 Partial Rebuild | Replace deteriorating copper shield wire with OPGW as well as deteriorating copper conductor with 1590 ACSS conductor | 2026 | Proposed | TBD | TBD | New
ES-23-LSP-116 | Asset Condition/Local Reliability | Connecticut | Transformer Additions/Replacements | Glenbrook - Transformer Replacements | Replace 115/13.2kV 46.7 MVA 2X transformer with 62.5 MVA transformer. | 2026 | Proposed | N/A | TBD | New
ES-23-LSP-117 | Local Reliability | Connecticut | New Substation | Mansfield Area Substation | Conversion of the Card to Mansfield corridor from 69-kV to 115-kV, expansion of the existing Mansfield to a ring bus by the addition of 4 circuit breakers, addition of a tie to a new UConn substation and associated upgrades ​ | 2026 | Concept | TBD | TBD | Yes
ES-23-LSP-118 | Asset Condition/Reliability | Connecticut | Transmission Line Project | 115kV Line 1753-1792 XLPE Replacement | Replace pipe-type cable (PTC) circuits between Glenbrook and Cedar Heights with solid dielectric cross-linked polyethylene (XLPE) technology. | 2027 | Planned | TBD | ES-22-T47, ES-22-T48 | Yes
ES-23-LSP-119 | Asset Condition/Local Reliability | Connecticut | Substation Reconfiguration/Expansion | Windsor Locks Substation - Expansion | Replace the existing tie breaker with two series breakers to improve load serving reliability. | 2027 | Proposed | TBD | TBD | New
ES-23-LSP-120 | Asset Condition/Local Reliability | Connecticut | Substation Reconfiguration/Expansion | Enfield Substation - Expansion | Replace the existing tie breaker with a PASS-M0 breaker to improve load serving reliability. | 2027 | Proposed | TBD | TBD | New
ES-23-LSP-121 | Local Reliability | Connecticut | Substation Reconfiguration/Expansion | Rocky Hill Substation Capacity Increase | Upgrade the substation to increase the substation load carrying capacity and to address transmission N-1 reliability violations. | 2027 | Concept | TBD | TBD | New
ES-23-LSP-122 | Asset Condition/Reliability | Connecticut | Transmission Line Project | 115kV Line 1270-1337 XLPE Replacement | Replace pipe-type cable (PTC) circuits between Triangle and Middle River with solid dielectric cross-linked polyethylene (XLPE) technology. | 2028 | Concept | TBD | TBD | Yes
ES-23-LSP-123 | Local Reliability | Connecticut | New Substation | Burrville 29J New Bulk Station | New 115 kV bulk substation in Torrington, CT with two 62.5 MVA transformers supplied via two 115 kV transmission circuits from the existing transmission circuits at Weingart Road Junction in Harwinton, CT​ | 2031 | Concept | TBD | TBD | No Changes
ES-23-LSP-124 | Asset Condition | New Hampshire | Transmission Line Project | D142 115kV Line Rebuild and Asset Condition Project | Rebuild the aging 115kV line with larger conductor | Dec-2022 | In-Service | 52.9 | ES-21-T40 | Yes
ES-23-LSP-125 | Asset Condition | New Hampshire | Transmission Line Project | E115 Tap 115kV Line Rebuild and Asset Condition Project | Rebuild the aging 115kV line with larger conductor and OPGW | May-2023 | In-Service | 5.7 | ES-21-T44 | Yes
ES-23-LSP-126 | Asset Condition | New Hampshire | Transmission Line Project | O154 115kV Line Rebuild and Asset Condition Project | Rebuild the aging 115kV line with larger conductor and OPGW | Dec-2023 | Under Construction | 51 | ES-21-T41 | No Changes
ES-23-LSP-127 | Asset Condition | New Hampshire | Transmission Line Project | W157 115kV Line Asset Condition Project | Replace deteriorating Alumoweld shieldwire with OPGW as well as deteriorating structures | Sep-2024 | Under Construction | 16.5 | N/A | New
ES-23-LSP-128 | Asset Condition | New Hampshire | Transmission Line Project | W179 115kV Line Rebuild and Asset Condition Project | Rebuild the aging 115kV line with larger conductor and OPGW | Dec-2024 | Under Construction | 81.5 | ES-21-T42, ES-23-T57 | Yes
ES-23-LSP-129 | Asset Condition | New Hampshire | Transmission Line Project | F190 115kV Line Rebuild and Asset Condition Project | Replace 0.15 miles of conductor and 2 deteriorating structures | Dec - 2024 | Planned | N/A | ES-23-T48 | New
ES-23-LSP-130 | Asset Condition | New Hampshire | Substation Reconfiguration/Expansion | Resistance Substation - Retirement | Resistance substation will be retired because all the equipment at the substation have reached the end of their useful life. All Resistance substation load will be transferred to the Portsmouth 115 kV substation. | Dec-2024 | Planned | TBD | ES-23-T49 | New
ES-23-LSP-131 | Asset Condition | New Hampshire | Transmission Line Project | J125 115kV Line Asset Condition Project | Replace deteriorated Laminated Wood Structures | Dec - 2024 | Proposed | TBD | N/A | New
ES-23-LSP-132 | Asset Condition/Reliability | New Hampshire | Substation Reconfiguration/Expansion | Monadnock Substation - Transformer replacements (Troy) | Replace the existing 115/34.5kV, 20 & 28 MVA transformers at Monadnock substation with two new 115/34.5kV, 62.5 MVA transformers. Add 5 breakers to have a ring bus configuration. | 2025 | Planned | TBD | ES-23-T47 | Yes
ES-23-LSP-133 | Asset Condition/Reliability | New Hampshire | Substation Reconfiguration/Expansion | White Lake Substation - Transformer replacements (Tamworth) | Replace the existing two 115/34.5kV, 28 MVA transformers at White Lake Substation with two new 115/34.5kV, 62.5 MVA transformers. Add two 115kV bus tie breakers. | 2025 | Proposed | TBD | TBD | No Changes
ES-23-LSP-134 | Asset Condition | New Hampshire | Transmission Line Project | S136 115kV Line Rebuild and Asset Condition Project | Rebuild the aging 115kV line with larger conductor | 2026 | Proposed | 139.8 | TBD | New
ES-23-LSP-135 | Asset Condition/Reliability | New Hampshire | Substation Reconfiguration/Expansion | Dover (Cocheco St.) Substation - Transformer replacements (Dover) | Replace the existing two 115/34.5kV, 44.8 MVA transformers at Dover (Cocheco Street) substation with two new 115/34.5kV, 62.5 MVA transformers. Add 4 breakers to have a ring bus configuration. | 2027 | Proposed | TBD | TBD | Yes
ES-23-LSP-136 | Load Growth and Reliability | New Hampshire | Substation Reconfiguration/Expansion | Laconia Substation - Transformer replacements (Laconia) | Replace the existing two 115/34.5kV, 44.8 MVA transformers at Laconia substation with two new 115/34.5kV, 62.5 MVA transformers. | 2027 | Concept | TBD | TBD | New
ES-23-LSP-137 | Load Growth and Reliability | New Hampshire | Transformer Additions/Replacements | South Milford Substation - Transformer Addition (Milford) | Add a second 115/34.5kV transformer at South Milford substation. Transformer to be a 62.5 MVA unit. | 2028 | Concept | TBD | TBD | No Changes